## COVER SHEET
Manufacteur: |  | Contractor / Company: |  |  | Vendor
Document No. |  |  |  |  | P.O. No.
EN20020IO01 |  | Daleel Oil Field Developmet
Client Document No. |  | Project |  |  | Sheet 1 of 5 | Rev. 0
461 Daleel
CABINET HARDWIRED PLC I/O LIST AP GAS RECOVERY
0 | First Issue |  | L. Barzasi | L. Balduzzi | M. Romelli | 2021-01-19
Rev. | Description |  | Prepared | Checked | Approved | Date

## NOTES
LEGEND |  | I/O TYPE
FLD | FIELD | 4 ÷ 20mA 2w | Transmitter Loop Powered by PLC
LCP | LOCAL CONTROL PANEL | 4 ÷ 20mA 4w | Transmitter External powered by other
MCC | MOTOR CONTROL CENTER
DCS | DISTRIBUTED CONTROL SYSTEM (BY CUSTOMER)
UCP | UNIT CONTROL PANEL (PLC CABINET)
ESD | EMERGENCY SHUT-DOWN
AI | ANALOG INPUT
AO | ANALOG OUTPUT
DI | DIGITAL INPUT
DO | DIGITAL OUTPUT
HW | HARDWIRE LINK
SL | SERIAL LINK
IS | INTRINSIC SAFE
NIS | NON INTRINSIC SAFE
IS FC | INTRINSIC SAFE FREE CONTACT
NIS FC | NON INTRINSIC SAFE FREE CONTACT
CCB | COMMON CONTROL BOX
ENI Iran B.V
NICO
P E D E C

## PLC IO LIST
#Pos | #TAG | #Descr | #Device | #Type | #Exec | #Location | #EU | #RangeL | #RangeH | #LL | #L | #H | #HH | #OFF | #ON | #Card | #PLCAddr | #Notes | #RedCard | #PLCRedAddr | #Circuit | #DigAlarm | #Tag1 | #Tag2 | #Tag3 | #Tag4 | #Tag5 | #Tag6 | #Tag7 | #Tag8 | #LL2 | #L2 | #H2 | #HH2
Pos. | Tag Number | Description Service | Device | Nature Of Signal | IS/NIS | Location | Engineering Unit | Range Min | Range Max | Low Low Set Point | Low Set Point | High Set Point | High High Set Point | STATE OFF | STATE ON | Type of PLC I/O Card | PLC Address (software) | Notes | Redundant PLC I/O Card | Rdundant PLC Address (software) | Circuit | Digital Alarm | Tag1 | Tag2 | TAg3 | Tag4 | Tag5 | Tag6 | Tag7 | Tag8 | Low Low Set Point | Low Set Point | High Set Point | High High Set Point |  | I/O Count
1 | VT-500A | Compressor Crankcase Vibration | VibrationTransmitter | 4 ÷ 20 mA | IS | FLD | kg/cm2 | -0.5 | 1.5 |  |  | 0.5 |  |  |  | AI1 | EW56 |  |  |  | mms |  | VT | zz | ZZ |  | 500A | zz |  |  | -0.1 | TBD | TBD | 0.3 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2 | LT-1626 | Suction Drum Level (Only Comp. A) | Differential Pressure Transmitter | 4 ÷ 20 mA | IS | FLD | kg/cm2 | 0 | 60 |  | 40.4 | 43.8 |  |  |  | AI1 | EW58 |  |  |  | water |  | Tag1: LT; Tag5: 1626 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
3 |  | SPARE |  | 4 ÷ 20 mA | IS | FLD | °C | 0 | 100 |  |  | 90 |  |  |  | AI1 | EW60 |  |  |  | water | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 |  | SPARE |  | 4 ÷ 20 mA | IS | FLD | kg/cm2 | 0 | 100 |  |  | 65 |  |  |  | AI1 | EW62 |  |  |  | mms | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | TE-800A | Lube Oil Temperature | PT100 | RTD | IS | FLD | °C | 0 | 200 |  |  | 140 | 230 |  |  | AI2 | EW16 |  |  |  | mms |  | Tag1: TE; Tag5: 800A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
6 | TE-801A | Compressor Bearing Temperature 1 | PT100 | RTD | IS | FLD | °C | 0 | 200 |  |  | 140 |  |  |  | AI2 | EW18 |  |  |  | mms |  | Tag1: TE; Tag5: 801A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
7 | TE-802A | Compressor Bearing Temperature 2 | PT100 | RTD | IS | FLD | % | 0 | 100 |  | 30 | 70 |  |  |  | AI2 | EW20 |  |  |  | mms |  | Tag1: TE; Tag5: 802A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | TE-401A | Cyinder 2 Cooling Water Temperature Outlet | PT100 | RTD | IS | FLD | kg/cm2 | 0 | 10 |  | 2.5 | 4 |  |  |  | AI2 | EW22 |  |  |  | mms |  | Tag1: TE; Tag5: 401A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
9 | TE-403A | Cyinder 1 Cooling Water Temperature Outlet | PT100 | RTD | IS | FLD | °C | 0 | 100 |  | 45 |  |  |  |  | AI3 | EW64 |  |  |  | mms |  | Tag1: TE; Tag5: 403A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
10 | TE-404A | Cooling Water Temperature Inlet Manifold | PT100 | RTD | IS | FLD |  |  |  |  | 5 | 5 |  |  |  | AI3 | EW66 |  |  |  | water |  | Tag1: TE; Tag5: 404A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
11 | TE-100A | Pulsation Damper Suction Temperature | PT100 | RTD | IS | FLD |  |  |  |  | 5 |  |  |  |  | AI3 | EW68 |  |  |  | water |  | Tag1: TE; Tag5: 100A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
12 |  | SPARE |  | RTD | IS | FLD | [9 empty] | AI3 | EW70 |  |  |  | mms | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | TE-1451A | Gas Discharge Temperature Cylinder 1 | PT100 | RTD | IS | FLD | kg/cm2 | 0 | 10 |  | 3.5 |  |  |  |  | AI4 | EW73 |  |  |  | oil |  | Tag1: TE; Tag5: 1451A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
14 | TE-1452A | Gas Discharge Temperature Cylinder 2 | lamp blue | RTD | IS | FLD | °C | 0 | 100 |  | 15 | 60 |  |  |  | AI4 | EW75 |  |  |  | oil |  | Tag1: TE; Tag5: 1452A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
15 | TE-501A | Piston Rod Packings Temperature Cylinder 1 | PT100 | RTD | IS | FLD | kg/cm2 | 0 | 2.5 |  |  | 0.5 |  |  |  | AI4 | EW77 |  |  |  | mms |  | Tag1: TE; Tag5: 501A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
16 | TE-500A | Piston Rod Packings Temperature Cylinder 2 | PT100 | RTD | IS | FLD | °C | 0 | 100 |  |  | 85 |  |  |  | AI4 | EW79 |  |  |  | mms |  | Tag1: TE; Tag5: 500A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
17 | TE-402A | Cyinder 1 Cooling Water Temperature Outlet | PT100 | RTD | IS | FLD | [8 empty] | CLOSED | AI5 | EW82 |  |  |  | mms |  | Tag1: TE; Tag5: 402A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
18 | TE-1454A | Gas Discharge Temperature Cylinder 2 | PT100 | RTD | IS | FLD | [8 empty] | OPEN | AI5 | EW84 |  |  |  | mms |  | Tag1: TE; Tag5: 1454A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
19 | TE-1453A | Gas Discharge Temperature Cylinder 1 | PT100 | RTD | IS | FLD | [8 empty] | CLOSED | AI5 | EW86 |  |  |  | gas |  | Tag1: TE; Tag5: 1453A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
20 |  | SPARE |  | RTD | IS | FLD | [8 empty] | OPEN | AI5 | EW88 |  |  |  | mms | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | TE-400A | Cyinder 2 Cooling Water Temperature Outlet | PT100 | RTD | IS | FLD | [9 empty] | AI4 | EW91 |  |  |  | oil |  | Tag1: TE; Tag5: 400A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
22 | TE-600A-1 | Main Motor Winding U Phase Temperature | PT100 | RTD | IS | FLD | [9 empty] | AI4 | EW93 |  |  |  | mms |  | Tag1: TE; Tag5: 600A-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
23 | TE-600A-2 | Main Motor Winding V Phase Temperature | PT100 | RTD | IS | FLD | [7 empty] | ALARM | NORMAL | AI4 | EW95 |  |  |  | mms |  | Tag1: TE; Tag5: 600A-2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
24 | TE-600A-3 | Main Motor Winding W Phase Temperature | PT100 | RTD | IS | FLD | [7 empty] | ALARM | NORMAL | AI4 | EW97 |  |  |  | oil |  | Tag1: TE; Tag5: 600A-3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
25 | PSLL-800A | Lube Oil Pressure | Pressure Switch | 24VDC | IS | FLD | [7 empty] | OFF | ON | DI1 | E8.0 |  |  |  | mms | LL | Tag1: PSLL; Tag5: 800A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
26 | PSLL-400A | Water Pressure | Pressure Switch | 24VDC | IS | FLD | [7 empty] | ALARM | NORMAL | DI1 | E8.1 |  |  |  | gas | LL | Tag1: PSLL; Tag5: 400A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
27 | PSHH-300A | Gas Discharge Pressure | Pressure Switch | 24VDC | IS | FLD | [7 empty] | OFF | ON | DI1 | E8.2 |  |  |  | mms | HH | Tag1: PSHH; Tag5: 300A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
28 | LSHH-1627 | Suction Drum Level Switch | Level Switch | 24VDC | IS | FLD | [7 empty] | ALARM | NOT ENGAGED | DI1 | E8.3 |  |  |  | oil | HH | Tag1: LSHH; Tag5: 1627 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
29 | PSLL-100A | Gas Suction Pressure | Pressure Switch | 24VDC | IS | FLD | [9 empty] | DI1 | E8.4 |  |  |  | water | LL | Tag1: PSLL; Tag5: 100A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
30 | PSH-300A | Gas Discharge Pressure | Pressure Switch | 24VDC | IS | FLD | [9 empty] | DI1 | E8.5 |  |  |  | mms | H | Tag1: PSH; Tag5: 300A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
31 | FSL-400A | Cooling Water Flow | Flow Switch | 24VDC | NIS | MCC | [8 empty] | RUNNING | DI1 | E8.6 |  |  |  | gas | L | Tag1: FSL; Tag5: 400A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
32 | LSL-400A | Cooling Water Level | Level Switch | 24VDC | NIS | MCC | [7 empty] | FAULT |  | DI1 | E8.7 |  |  |  | mms | L | Tag1: LSL; Tag5: 400A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
33 | PSL-800A | Lube Oil Pressure | Pressure Switch | 24VDC | NIS | MCC | [7 empty] | Unavailable | Available | DI1 | E9.0 |  |  |  | water | L | Tag1: PSL; Tag5: 800A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
34 | DPSH-800A | Oil Filter Pressure Drop | Differential Pressure Switch | 24VDC | NIS | MCC | [8 empty] | ON | DI1 | E9.1 |  |  |  | water | H | Tag1: DPSH; Tag5: 800A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
35 | LSL-800A | Lube Oil Level | Level Switch | 24VDC | NIS | MCC | [7 empty] | FAULT |  | DI1 | E9.2 |  |  |  | water | L | Tag1: LSL; Tag5: 800A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
36 | TSH-800A | Lube Oil Heater Safety Temp. Switch | Temperature Switch | 24VDC | NIS | MCC | [7 empty] | Unavailable | Available | DI1 | E9.3 |  |  |  | mms | H | Tag1: TSH; Tag5: 800A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
37 | TC-800A | Lube Oil Heater Regulation Temp. Switch | Temperature Switch | 24VDC | NIS | MCC | [9 empty] | DI1 | E9.4 | [5 empty] | Tag1: TC; Tag5: 800A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
38 | PSL-400A | Cooling Water Pressure | Pressure Switch | 24VDC | NIS | MCC | [9 empty] | DI1 | E9.5 |  |  |  | oil | L | Tag1: PSL; Tag5: 400A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
39 | TC-400A | Cooling Water Heater Regulation Temp. Switch | Temperature Switch | 24VDC | NIS | MCC | [8 empty] | RUNNING | DI1 | E9.6 | [5 empty] | Tag1: TC; Tag5: 400A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
40 | GSH-1A | Junction Box Gas Detector Alarm | Gas Detectior Switch | 24VDC | NIS | MCC | [7 empty] | FAULT |  | DI1 | E9.7 |  |  |  | mms | H | Tag1: GSH; Tag5: 1A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
41 |  | SPARE |  | 24VDC | NIS | MCC | [7 empty] | Unavailable | Available | DI2 | E10.0 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 |  | SPARE |  | 24VDC | NIS | MCC | [8 empty] | ON | DI2 | E10.1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 |  | SPARE |  | 24VDC | NIS | MCC | [7 empty] | FAULT |  | DI2 | E10.2 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 |  | SPARE |  | 24VDC | NIS | MCC | [7 empty] | Unavailable | Available | DI2 | E10.3 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 |  | SPARE |  | 24VDC | NIS | MCC | [8 empty] | RUNNING | DI2 | E10.4 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | HS-1A | Water & Lube Oil Heaters Diable / Enable | 2Pos. Selector Switch | 24VDC | NIS | MCC | [7 empty] | Unavailable | Available | DI2 | E10.5 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | bar: Tag1; Tag5
47 | HS-2A | Lube Oil Pump Start P.B. | Green Pushbutton | 24VDC | NIS | MCC | [9 empty] | DI2 | E10.6 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | bar: Tag1; Tag5
48 | HS-3A | Lube Oil Pump Stop P.B. | Red Pushbutton | 24VDC | NIS | MCC | [9 empty] | DI2 | E10.7 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | bar: Tag1; Tag5
49 | HS-4A-1 | Water Pump Selection PM3-PM4 | 2Pos. Selector Switch | 24VDC | IS | FLD | °C | 0 | 200 |  |  | 140 |  |  |  | DI2 | E11.0 | [5 empty] | Tag1: HS; Tag5: 4A-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
50 | HS-4A-2 | Water Pump Selection PM3-PM4 |  | 24VDC | IS | FLD | °C | 0 | 200 |  |  | 140 |  |  |  | DI2 | E11.1 | [5 empty] | Tag1: HS; Tag5: 4A-2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
51 | HS-5A | Water Pump PM3-PM4 Start P.B. | Green Pushbutton | 24VDC | IS | FLD | °C | 0 | 200 |  |  | 140 |  |  |  | DI2 | E11.2 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | bar: Tag1; Tag5
52 | HS-6A | Water Pump PM3-PM4 Stop P.B. | Red Pushbutton | 24VDC | IS | FLD | °C | 0 | 200 |  |  | 140 |  |  |  | DI2 | E11.3 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | bar: Tag1; Tag5
53 | HS-9A | Compressor Motor Start P.B. | Green Pushbutton | 24VDC | [11 empty] | DI2 | E11.4 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | bar: Tag1; Tag5
54 | HS-10A | Compressor Motor Stop P.B. | Red Pushbutton | 24VDC | [11 empty] | DI2 | E11.5 | [5 empty] | Tag1: HS; Tag5: 10A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
55 | HS-11A | Reset P.B. | Black Pushbutton | 24VDC | [11 empty] | DI2 | E11.6 | [5 empty] | Tag1: HS; Tag5: 11A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
56 | HS-12A | Ack P.B. | Black Pushbutton | 24VDC | [11 empty] | DI2 | E11.7 | [5 empty] | Tag1: HS; Tag5: 12A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
57 | HS-13A | Test Lamps P.B. | Black Pushbutton | 24VDC | [11 empty] | DI3 | E12.0 | [5 empty] | Tag1: HS; Tag5: 13A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
58 | HS-14A | Emergency Stop Local P.B. | Red Mushroom Pushbutton | 24VDC | [11 empty] | DI3 | E12.1 |  |  |  | gas | HH | Tag1: HS; Tag5: 14A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
59 | HS-15A | Nitrogen Bypass | Black Pushbutton | 24VDC | [11 empty] | DI3 | E12.2 | [5 empty] | Tag1: HS; Tag5: 15A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
60 | HS-16A | Reset Bypass | Black Pushbutton | 24VDC | [11 empty] | DI3 | E12.3 | [5 empty] | Tag1: HS; Tag5: 16A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
61 | HS-17A | Manual Tank Make-Up | Black Pushbutton | 24VDC | [11 empty] | DI3 | E12.4 | [5 empty] | Tag1: HS; Tag5: 17A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
62 |  | SPARE |  | 24VDC | [11 empty] | DI3 | E12.5 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 |  | SPARE |  | 24VDC | [11 empty] | DI3 | E12.6 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 |  | SPARE |  | 24VDC | [11 empty] | DI3 | E12.7 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | KLO-HFA | Lube Oil Heater Feedback | Dry Contact | 24VDC | [11 empty] | DI3 | E13.0 | [5 empty] | Tag1: KLO; Tag5: HFA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
66 | KCW-HFA | Cooling Water Heater On Feedback | Dry Contact | 24VDC | [11 empty] | DI3 | E13.1 | [5 empty] | Tag1: KCW; Tag5: HFA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
67 | KLO-PFA | Lube Oil Pump On Feedback | Dry Contact | 24VDC | [11 empty] | DI3 | E13.2 | [5 empty] | Tag1: KLO; Tag5: PFA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
68 | KWP-3A | Water Pump PM3 Feedback | Dry Contact | 24VDC | [11 empty] | DI3 | E13.3 | [5 empty] | Tag1: KWP; Tag5: 3A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
69 | KWP-4A | Water Pump PM4 Feedback | Dry Contact | 24VDC | [11 empty] | DI3 | E13.4 | [5 empty] | Tag1: KWP; Tag5: 4A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
70 | EFP-3A | Water Pump PM3 Electric Failure | Dry Contact | 24VDC | [11 empty] | DI3 | E13.5 |  |  |  | mms | LL | Tag1: EFP; Tag5: 3A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
71 | EFP-4A | Water Pump PM4 Electric Failure | Dry Contact | 24VDC | [11 empty] | DI3 | E13.6 |  |  |  | mms | LL | Tag1: EFP; Tag5: 4A | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
72 | KC-RFA | Compressor Running Feedback | Dry Contact | 24VDC | [11 empty] | DI3 | E13.7 | [5 empty] | Tag1: KC; Tag5: RFA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
73 | PSL-CUST | Pressure Switch Drum Off Customer | Pressure Switch | 24VDC | [11 empty] | DI4 | E14.0 | [5 empty] | Tag1: PSL; Tag5: CUST | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
74 | PSH-CUST | Pressure Switch Drum On Customer | Pressure Switch | 24VDC | [11 empty] | DI4 | E14.1 | [5 empty] | Tag1: PSH; Tag5: CUST | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
75 | HS-14.1 | Emergency Shutdown DCS P.B. | Red Mushroom Pushbutton | 24VDC | [11 empty] | DI4 | E14.2 |  |  |  | mms | HH | Tag1: HS; Tag5: 14.1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
76 |  | SPARE |  | 24VDC | [11 empty] | DI4 | E14.3 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 |  | SPARE |  | 24VDC | [11 empty] | DI4 | E14.4 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 |  | SPARE |  | 24VDC | [11 empty] | DI4 | E14.5 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SPARE |  | 24VDC | [11 empty] | DI4 | E14.6 | [17 empty] | FORMULE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SPARE |  | 24VDC | [11 empty] | DI4 | E14.7 | [17 empty] | TOTALI | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 43 | 0
| HS-18A | Capacity Control AUTO / MANUAL | 2Pos. Selector Switch | 24VDC | [11 empty] | DI4 | E15.0 | [5 empty] | Tag1: HS; Tag5: 18A
| HS-19A-1 | Loading Position 25% | 4Pos. Selector Switch | 24VDC | [11 empty] | DI4 | E15.1 | [5 empty] | Tag1: HS; Tag5: 19A-1
| HS-19A-2 | Loading Position 50% |  | 24VDC | [11 empty] | DI4 | E15.2 | [5 empty] | Tag1: HS; Tag5: 19A-2
| HS-19A-3 | Loading Position 75% |  | 24VDC | [11 empty] | DI4 | E15.3 | [5 empty] | HS |  |  |  | 19A-3 | [8 empty] | SAI | SAO | SDI | SDO | RTD | AI | AO | DI | DO
| HS-19A-4 | Loading Position 100% |  | 24VDC | [11 empty] | DI4 | E15.4 | [5 empty] | HS |  |  |  | 19A-4 | [7 empty] | canali x scheda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SPARE |  | 24VDC | [11 empty] | DI4 | E15.5 | [17 empty] | qty schede | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SPARE |  | 24VDC | [11 empty] | DI4 | E15.6 | [17 empty] | Disponibili | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SPARE |  | 24VDC | [11 empty] | DI4 | E15.7 | [17 empty] | Usati | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 43 | 0
| PALL-800A | Very Low Lube Oil Pressure | Red Lamp | 24VDC | [11 empty] | DO1 | A0.0 | [5 empty] | PALL |  |  |  | 800A | [7 empty] | SPARE | 0 | 0 | 0 | 0 | 0 | -20 | 0 | -43 | 0
| TAHH-800A | Very High Lube Oil Temperature | Red Lamp | 24VDC | [11 empty] | DO1 | A0.1 | [5 empty] | TAHH |  |  |  | 800A | [7 empty] | % SPARE SU SCHEDE | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| TAHH-801A | Very High Compressor Bearing Temperature 1 | Red Lamp | 24VDC | [11 empty] | DO1 | A0.2 | [5 empty] | TAHH |  |  |  | 801A | [7 empty] | % SPARE SU USATI | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | -100 | #DIV/0! | -100 | #DIV/0!
| TAHH-802A | Very High Compressor Bearing Temperature 2 | Red Lamp | 24VDC | [11 empty] | DO1 | A0.3 | [5 empty] | TAHH |  |  |  | 802A
| PALL-400A | Very Low Water Pressure | Red Lamp | 24VDC | [11 empty] | DO1 | A0.4 | [5 empty] | PALL |  |  |  | 400A
| TAHH-1454A | Very High Gas Discharge Temp. 1st Stage Cyl. n.2 | Red Lamp | 24VDC | [11 empty] | DO1 | A0.5 | [5 empty] | TAHH |  |  |  | 1454A
| TAHH-1453A | Very High Gas Discharge Temp. 1st Stage Cyl. n.1 | Red Lamp | 24VDC | [11 empty] | DO1 | A0.6 | [5 empty] | TAHH |  |  |  | 1453A
| PAHH-300A | Very High Gas Discharge Pressure | Red Lamp | 24VDC | [11 empty] | DO1 | A0.7 | [5 empty] | PAHH |  |  |  | 300A
| TAHH-400A | Very High Cooling Water Temp. 1st Stage Cyl. n.2 | Red Lamp | 24VDC | [11 empty] | DO1 | A1.0 | [5 empty] | TAHH |  |  |  | 400A
| TAHH-402A | Very High Cooling Water Temp. 1st Stage Cyl. n.1 | Red Lamp | 24VDC | [11 empty] | DO1 | A1.1 | [5 empty] | TAHH |  |  |  | 402A
| LAHH-1627 | Very high Suction Drum Level | Red Lamp | 24VDC | [11 empty] | DO1 | A1.2 | [5 empty] | LAHH |  |  |  | 1627
| PALL-100A | Very Low Gas Suction Pressure | Red Lamp | 24VDC | [11 empty] | DO1 | A1.3 | [5 empty] | PALL |  |  |  | 100A
| TAH-1451A | High Gas Discharge Temp. 1st Stage Cyl. n.1 | Yellow Lamp | 24VDC | [11 empty] | DO1 | A1.4 | [5 empty] | TAH |  |  |  | 1451A
| TAH-1452A | High Gas Discharge Temp. 1st Stage Cyl. n.2 | Yellow Lamp | 24VDC | [11 empty] | DO1 | A1.5 | [5 empty] | TAH |  |  |  | 1452A
| PAH-300A | High Gas Discharge Pressure | Yellow Lamp | 24VDC | [11 empty] | DO1 | A1.6 | [5 empty] | PAH |  |  |  | 300A
| TAH-401A | High Cooling Water Temp. 1st Stage Cyl. n.2 | Yellow Lamp | 24VDC | [11 empty] | DO1 | A1.7 | [5 empty] | TAH |  |  |  | 401A
| TAH-403A | High Cooling Water Temp. 1st Stage Cyl. n.1 | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.0 | [5 empty] | TAH |  |  |  | 403A
| TAL-404A | Low Cooling Water Temp. Inlet Manifold | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.1 | [5 empty] | TAL |  |  |  | 404A
| FAL-400A | Low Cooling Water Flow | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.2 | [5 empty] | FAL |  |  |  | 400A
| LAL-400A | Low Cooling Water Level | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.3 | [5 empty] | LAL |  |  |  | 400A
| PAL-800A | Low Lube Oil Pressure | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.4 | [5 empty] | PAL |  |  |  | 800A
| DPAH-800A | High Oil Filter Pressure Drop | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.5 | [5 empty] | DPAH |  |  |  | 800A
| LAL-800A | Low Lube Oil Level | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.6 | [5 empty] | LAL |  |  |  | 800A
| TAH-801A | Compressor Bearing High Temperature 1 | Yellow Lamp | 24VDC | [11 empty] | DO2 | A2.7 | [5 empty] | TAH |  |  |  | 801A
| TAH-802A | Compressor Bearing High Temperature 2 | Yellow Lamp | 24VDC | [11 empty] | DO2 | A3.0 | [5 empty] | TAH |  |  |  | 802A
| TAH-500A | Piston Rod Packings High Temperature | Yellow Lamp | 24VDC | [11 empty] | DO2 | A3.1 | [5 empty] | TAH |  |  |  | 500A
| TAH-501A | Piston Rod Packings High Temperature | Yellow Lamp | 24VDC | [11 empty] | DO2 | A3.2 | [5 empty] | TAH |  |  |  | 501A
| VAHH-500A | Very High Compressor Grankcase Vibration | Red Lamp | 24VDC | [11 empty] | DO2 | A3.3 | [5 empty] | VAHH |  |  |  | 500A
| TAH-600A | High Compressor Motor Winding Temp. | Yellow Lamp | 24VDC | [11 empty] | DO2 | A3.4 | [5 empty] | TAH |  |  |  | 600A
| LAH-1626 | High Suction Drum Level | Yellow Lamp | 24VDC | [11 empty] | DO2 | A3.5 | [5 empty] | LAH |  |  |  | 1626
| TAH-800A | Lube Oil Heater High Temperature | Yellow Lamp | 24VDC | [11 empty] | DO2 | A3.6 | [5 empty] | TAH |  |  |  | 800A
| TAH-404A | High Cooling Water Manifold | Yellow Lamp | 24VDC | [11 empty] | DO2 | A3.7 | [5 empty] | TAH |  |  |  | 404A
| H-1A | Lube Oil Heater On | Green Lamp | 24VDC | [11 empty] | DO3 | A4.0 | [5 empty] | H |  |  |  | 1A
| H-2A | Cooling Water Heater On | Green Lamp | 24VDC | [11 empty] | DO3 | A4.1 | [5 empty] | H |  |  |  | 2A
| H-3A | Aux. Lube Oil Pump On | Green Lamp | 24VDC | [11 empty] | DO3 | A4.2 | [5 empty] | H |  |  |  | 3A
| H-4A | Aux. Lube Oil Pump Stopped | Red Lamp | 24VDC | [11 empty] | DO3 | A4.3 | [5 empty] | H |  |  |  | 4A
| H-5A | Cooling Water Pump PM3 Running | Green Lamp | 24VDC | [11 empty] | DO3 | A4.4 | [5 empty] | H |  |  |  | 5A
| H-6A | Cooling Water Pump PM3 Stopped | Red Lamp | 24VDC | [11 empty] | DO3 | A4.5 | [5 empty] | H |  |  |  | 6A
| H-7A | Cooling Water Pump PM4 Running | Green Lamp | 24VDC | [11 empty] | DO3 | A4.6 | [5 empty] | H |  |  |  | 7A
| H-8A | Cooling Water Pump PM4 Stopped | Red Lamp | 24VDC | [11 empty] | DO3 | A4.7 | [5 empty] | H |  |  |  | 8A
| H-9A | Compressor Running | Green Lamp | 24VDC | [11 empty] | DO3 | A5.0 | [5 empty] | H |  |  |  | 9A
| H-10A | Compressor Stopped Long Time Unloading | Red Lamp | 24VDC | [11 empty] | DO3 | A5.1 | [5 empty] | H |  |  |  | 10A
| PAL-400A | Low Water Pressure | Yellow Lamp | 24VDC | [11 empty] | DO3 | A5.2 | [5 empty] | PAL |  |  |  | 400A
| HSV-100A | Compressor Loading Cylinder 1 CE | Green Lamp | 24VDC | [11 empty] | DO3 | A5.3 | [5 empty] | HSV |  |  |  | 100A
| HSV-102A | Compressor Loading Cylinder 2 HE | Green Lamp | 24VDC | [11 empty] | DO3 | A5.4 | [5 empty] | HSV |  |  |  | 102A
| HSV-101A | Compressor Loading Cylinder 1 HE | Green Lamp | 24VDC | [11 empty] | DO3 | A5.5 | [5 empty] | HSV |  |  |  | 101A
| HSV-103A | Compressor Loading Cylinder 2 CE | Green Lamp | 24VDC | [11 empty] | DO3 | A5.6 | [5 empty] | HSV |  |  |  | 103A
| H-14A | Emergency Stop | Red Lamp | 24VDC | [11 empty] | DO3 | A5.7 | [5 empty] | H |  |  |  | 14A
| H15-A | Bypass for PSLL-100 & PSHH-300 & PSH-300 | White Lamp | 24VDC | [11 empty] | DO4 | A6.0 | [5 empty] | H15 |  |  |  | A
| READY | Ready To Start | White Lamp | 24VDC | [11 empty] | DO4 | A6.1
|  | SPARE |  | 24VDC | [11 empty] | DO4 | A6.2
|  | SPARE |  | 24VDC | [11 empty] | DO4 | A6.3
| K-1A | Lube Oil Heater ON / OFF Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A6.4 | [5 empty] | K |  |  |  | 1A
| K-2A | Cooling Water Heater ON / OFF Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A6.5 | [5 empty] | K |  |  |  | 2A
| K-3A | Aux Lube Oil Pump OFF / ON Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A6.6 | [5 empty] | K |  |  |  | 3A
| K-4A | Cooling Water PM3 OFF / ON Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A6.7 | [5 empty] | K |  |  |  | 4A
| K-5A | Fan Cooler Motor OFF / ON Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.0 | [5 empty] | K |  |  |  | 5A
| K-6A | Cooling Water PM4 OFF / ON Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.1 | [5 empty] | K |  |  |  | 6A
| K-7A | Stop Compressor Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.2 | [5 empty] | K |  |  |  | 7A
| K-8A | Start Compressor Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.3 | [5 empty] | K |  |  |  | 8A
| K-9A | Compressor Motor Heater ON / OFF Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.4 | [5 empty] | K |  |  |  | 9A
| K-10A | Loading Sol. Valve SV-100 Cyl. n.1 - CE Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.5 | [5 empty] | K |  |  |  | 10A
| K-12A | Loading Sol. Valve SV-101 Cyl. n.1 - HE Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.6 | [5 empty] | K |  |  |  | 12A
| K-11A | Loading Sol. Valve SV-102 Cyl. n.2 - HE Command | Relay Dry Contact | 24VDC | [11 empty] | DO4 | A7.7 | [5 empty] | K |  |  |  | 11A
| K-13A | Loading Sol. Valve SV-103 Cyl. n.2 - CE Command | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.0 | [5 empty] | K |  |  |  | 13A
| K-14A | Water Solenoid Valve SV- 400 Command | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.1 | [5 empty] | K |  |  |  | 14A
| K-15A | Discharge Condensate Sol. Valve PV-100A Command | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.2 | [5 empty] | K |  |  |  | 15A
| K-16A | Discharge Condensate Sol. Valve PV-200A Command | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.3 | [5 empty] | K |  |  |  | 16A
| K-17A | Discharge Condensate Sol. Valve PV-201A Command | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.4 | [5 empty] | K |  |  |  | 17A
| K-18A | Common Alarms | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.5 | [5 empty] | K |  |  |  | 18A
| K-19A | Common Trips | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.6 | [5 empty] | K |  |  |  | 19A
| K-20A | Horn | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A8.7 | [5 empty] | K |  |  |  | 20A
| K-21A | Compressor Ready to Start | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A9.0 | [5 empty] | K |  |  |  | 21A
| K-22A | Suction Drum Very High Level | Relay Dry Contact | 24VDC | [11 empty] | DO5 | A9.1 | [5 empty] | K |  |  |  | 22A
|  | SPARE |  | 24VDC | [11 empty] | DO5 | A9.2
|  | SPARE |  | 24VDC | [11 empty] | DO5 | A9.3
|  | SPARE |  | 24VDC | [11 empty] | DO5 | A9.4
|  | SPARE |  | 24VDC | [11 empty] | DO5 | A9.5
|  | SPARE |  | 24VDC | [11 empty] | DO5 | A9.6
|  | SPARE |  | 24VDC | [11 empty] | DO5 | A9.7
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.0
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.1
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.2
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.3
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.4
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.5
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.6
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A10.7
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.0
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.1
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.2
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.3
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.4
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.5
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.6
|  | SPARE |  | 24VDC | [11 empty] | DO6 | A11.7
ENI Iran B.V
NICO
P E D E C
Note on C2: Microsoft Office User: TUTTO MAIUSCOLO

## Parameter
Tipo Scheda
AI1
AO1
DI1
DO1
SAI1
SAO1
SDI1
SDO1
RTD
Device
PRESSURE TRANSMITTER
WET CONTACT
DRY CONTACT

## CALCOLO SCHEDE (hidden)
| ATTUALI | sup | 20% | IN | N | DISPONIBILI |  |  |  |  | VECCHI | sup | 20% | DISPONIBILI |  | SEGNALI AGGIUNTI |  | VECCHIE |  | 20% | DISPONIBILI
AI | 22 |  | 26.4 | 8 | 4 | 32 | 1 |  | 11 | AI | 11 | 0 | 13.2 | 16 | 1 | -3 | AI | 14 |  | 16.8 | 24 | 1
SAI | 21 |  | 25.2 | 4 | 7 | 28 | 1 |  | 3 | SAI | 17 | 1 | 21.6 | 24 | 1 | 8 | SAI | 10 |  | 12 | 12 | 1
AO | 3 |  | 3.6 | 4 | 1 | 4 | 1 |  | 1 | AO | 1 | 1 | 2.4 | 4 | 1 | 0 | AO | 2 |  | 2.4 | 4 | 1
DI | 16 |  | 19.2 | 32 | 1 | 32 | 1 |  | 0 | DI | 0 | 16 | 19.2 | 32 | 1 | -1 | DI | 17 |  | 20.4 | 32 | 1
SDI | 20 |  | 24 | 16 | 2 | 32 | 1 |  | 4 | SDI | 14 | 2 | 19.2 | 32 | 1 | 10 | SDI | 6 |  | 7.2 | 16 | 1
DO | 25 |  | 30 | 32 | 1 | 32 | 1 |  | 1 | DO | 0 | 24 | 28.8 | 32 | 1 | -2 | DO | 26 |  | 31.2 | 32 | 1
SDO | 17 |  | 20.4 | 8 | 3 | 24 | 1 |  | 4 | SDO | 11 | 2 | 15.6 | 16 | 1 | 6 | SDO | 7 |  | 8.4 | 8 | 0
[6 empty] | 184 |  |  | 24 |  |  |  |  | 156 |  | 18 |  | 82
NUMERO SCHEDE | 20% | DISPONIBILE
19 | [15 empty] | 42
4
1
24 | 28.8 | 32 | 1
|  |  | pin vuoti |  |  | MESSI |  | TOTALE | DOPPIO | messi | da mettere | [8 empty] | pin vuoti | MESSI |  | TOTALE
X-AI-1 | 16 | 19.2 | 3.2 |  |  | 4 |  | 20 | 40 | 40 | 0 | [6 empty] | 17 | 20.4 | 3.4 | 4 |  | 21
X-MCC-1 | 60 | 72 | 12 |  |  | 12 |  | 72 | 144 | 106 | 38 | [6 empty] | 44 | 52.8 | 8.8 | 9 |  | 53
X-AI-SIL-1 | 22 | 26.4 | 4.4 |  |  | 5 |  | 27 | 54 | 44 | 10 | [6 empty] | 25 | 30 | 5 | 5 |  | 30
X-AI-SIL-SI-1 | 4 | 4.8 | 0.8 |  |  | 1 |  | 5 | 10 | 0 | 10
X-AO-1 | 2 | 2.4 | 0.4 |  |  | 1 |  | 3 | 6 | 6 | 0 | [6 empty] | 2 | 2.4 | 0.4 | 1 |  | 3
X-DCS-1 | 12 | 14.4 | 2.4 |  |  | 3 |  | 15 | 30 | 28 | 2 | [6 empty] | 11 | 13.2 | 2.2 | 3 |  | 14
X-DI-1 | 10 | 12 | 2 |  |  | 2 |  | 12 | 24 | 24 | 0 | [6 empty] | 10 | 12 | 2 | 2 |  | 12
X-DI-SIL-1 | 30 | 36 | 6 |  |  | 6 |  | 36 | 72 | 74 | -2 | [6 empty] | 30 | 36 | 6 | 7 |  | 37
X-DO-1 | 4 | 4.8 | 0.8 |  |  | 1 |  | 5 | 10 | 10 | 0 | [6 empty] | 4 | 4.8 | 0.8 | 1 |  | 5
X-DO-SIL-1 | 21 | 25.2 | 4.2 |  |  | 5 |  | 26 | 52 | 34 | 18 | [6 empty] | 16 | 19.2 | 3.2 | 4 |  | 20
INTERNI AL QUADRO | 3
184